## parameters
Parameter | Value | Units | Comment
SITE
location_name | Woomera | N/A
latitude | -31.2 | degrees | Make sure that this is the same with the climate file used bt SolarPILOT
longitude | 136.8167 | degrees | Make sure that this is the same with the climate file used bt SolarPILOT
timezone_offset | 9.5 | hours | hours before GMT. Make sure that this is the same as the SolarPILOT file
hr_z0 | 50 |  | ratio between the reference height and the surface roughness
PLANT
stowangle | 10 | degrees | sun elevation angle at which heliostats go to stow position
stow_tilt | 90 | degrees | tilt angle for the stowing of the heliostats at night (must be close to 90)
receiver_type | External cylindrical | - | shape of receiver [External cylindrical] or [Flat plate]
receiver_tower_height | 195 | m | height of receiver tower (from paper)
receiver_height | 30.5 | m | height of the receiver panels
receiver_width_diameter | 15.8 | m | width of receiver [flat plate] or diameter of receiver [external receiver]
receiver_thermal_losses | 105 | MW | thermal losses of receiver (assumed constant)
power_block_efficiency | 0.35 | - | overall efficiency of power block (thermal -> electricity)
minimum_receiver_power | 210 | MWt | Minimum thermal input to start receiver
maximum_receiver_power | 1000 | MWt | Maximum thermal input to receiver before defocusing must occur
heliostat_aim_point_strategy | Image size priority | - | One of: Simple aim points,Sigma aiming,Probability shift,Image size priority,Keep existing,Freeze tracking
HELIOSTATS
heliostat_height | 11.3 | m | height of the heliostat
heliostat_width | 10.4 | m | width of the heliostat
nominal_reflectance | 0.95 | - | Clean reflectance of the heliostat
hamaker_glass | 6.5e-20 | J | Hamaker constant of quartz (dust)
poisson_glass | 0.27 |  | Poisson ration of quartz (dust)
youngs_modulus_glass | 80100000000 | N/m2 | Young's modulus of quartz (dust)
CONSTANTS
air_density | 1.2047 | kg/m^3 | air density at T=293K and p=1 atm
air_dynamic_viscosity | 1.817e-05 | Pa*s | dynamic viscosity of air at T=293K and p=1 atm
mean_free_path_air | 6.5e-08 | m | free mean path in air [m]
I_solar | 1367.7 | W/m2 | extraterrestrial solar constant
A1_A2_A3 | 1.257;0.4;0.55 |  | slip correction factor coefficients
k_boltzman | 1.381e-23 | J/K | Boltzman constant
k_von_karman | 0.4 |  | von Karman constant
N_iter | 1000 |  | max interations to compute the gravitational settling velocity
tol | 0.005 |  | tolerance to reach convergence in the gravitational settling velocity computation
Re_Limit | 0.1;2;500 |  | Reynolds limit values to choose among correlations for the drag coefficient
alpha_EIM | 400 |  | factor for impaction factor computation
beta_EIM | 2 |  | factor for impaction factor computation
eps0 | 3 |  | empirical factor for boundary layer resistance computation
D0 | 4e-10 | m | common value of separation distance (Ahmadi)
loss_model | geometry |  | Either "geometry" or "mie"